## Sheet1
ID | Start time | Completion time | Email | Name | Last modified time | Name and address of the Research Infrastructure: | BMS Brand - Vendor | Year of the production | Year of the installation | Type of main processors | Type of I/O modules | Type of communication bus | Type of main BMS communication protocol (if more, please specify) | Type of secondary BMS communication protocol (if more, please specify) | Type of the main SCADA and related SW | Type of the secondary SCADA and related SW | Is remoted acces/supervision implemented? | Please specify implemented remoted acces/supervision in more detail. | How are the user accounts managed? | How is the BMS/SCADA integrated to the facility network infrastructure? | How is the administration of the network infrastructure secured? | How is the BMS/SCADA system managed? | Is SW/HW interface implemented for cooperation with other control systems used in the building? | Please specify the SW/HW interface cooperation with other control systems. | Data repository status | Are the data from the database further processed? | Please specify the further processing of the data. | Is an automatized energy management system implemented? | What type of connection of eventual sources of energy is implemented? | Please specify the connection via communications protocol in more detail. | Air conditioning | Please indicate the major technological connection of air conditioning units. | Source of heat / Heating system | Source of the cool water / Cooling systems | Please specify the cooling source. | Please specify the work output of ice banks. | Please specify the cooling source.2 | Cogeneration unit | Please specify the cogeneration unit type. | Active blind control systems or any other active facade systems | Please specify the installed active blind control/facade systems in more detail. | Total floor area of the building and its further categorization. Please provide values for each category and detailed information about what each parameter value specifically refers to. Please pr... | Indoor climatic conditions of the research spaces and cleanrooms of the building. Please provide projected values with acceptable deviations for each category. | Outdoor climatic conditions | Please provide real-world data, ideally for the years 2023 and 2022, showing actual temperature and humidity values for outdoor environments as well as indoor environments - research spaces and cl... | Please specify (or provide a qualified estimate) the amount of energy (both electricity and gas) required for maintaining indoor climatic conditions, expressed as a percentage of the total energy ... | Cleanrooms clasification | Please provide the HVAC (Heating, Ventilation and Air Conditioning) system diagram to us. | Please indicate methods of humidity control (humidification, dehumidification) and principles of air purification, as well as potential air disinfection in your HVAC systems. | On what basis is HVAC maintenance carried out? | Do you use Heat Recovery at your building? | Please specify the technology of Heat Recovery used. | Do you use local air conditioning units? | Please specify the Air exchange of the unit (in m3/h) and the total number of units in the building. | Do you perform a Life Cycle Assessment (LCA) as a part of your operations? | Is the LCA conducted for the entire facility, specific equipment (e.g. laser or accelerator), or another component? Please specify. | Please specify the following details regarding the conducted LCA. | Please provide LCA Report to us. | Please provide the following data. | Do you have already made a carbon intensity calculation of the usage of your cryogenic liquids ? | Name of the person that will be in charge of interacting with the consultant in charge of the environmental print study.
1 | 2024-10-17 15:18 | 2024-10-17 15:19 | anonymous
2 | 2024-11-18 12:29 | 2024-11-18 12:44 | anonymous |  |  | ELI_ALPS Hungary 6728 Szeged, Wolfgang Sandner Str. 3. | Honeywell Enterprise Buildings Integrator _ Release 600.1 (EBI R600) - WellTech Zrt. | 2019 | 2016 | Intel(R) Xeon(R) E-2244G CPU @ 3.80GHz, Honeywell CLAXHAWK650E, Honeywell CLAXHAWKIF485, Honeywell CLNXHAWK8-250 | Honeywell CLEA2014B32, Honeywell CLEA2026B31, Honeywell CLIOP821A, Honeywell CLIOP822A, Honeywell CLIOP823A, Honeywell CLIOP824A, Honeywell CLIOP830A | BacNET, MODBUS, LON | TCP/IP | BacNet | Honeywell Enterprise Buildings Integrator - Release 600.1 | n.a. | yes | VPN | for administrator | BMS/SCADA is a part of the network infrastructure | by IT | by external company | yes | ModBus, dry contact - prevacuum system, fire alarm system, radiation protection system, RWA system, fire extinguishing system ; via SNMP - research technology alarm | data are recorded periodically | no |  | no | discreetly |  | yes | Temperature, humidity, air pressure sensors (in/out) | Boiler room - gas/solid fuel;Heat pumps; | cooling source | CIAT LX 4800X-STD R134A, CIAT LW-LWP 4800BX-2-HPS, CIAT LX-4200X-STD, CIAT ILD 600V, YORK YVAA 0765 CRV50BHVN, YORK AQVL 115 | n.a. | n.a. | no |  | yes | Shading blinds regulation based on light intensity - on 3 sides and the top of building C glass surfaces | i. Total floor area in m2: 23 404 ii. Floor area of research spaces in m2: 293 (labs, labcoat changers) iii. Floor area of cleanrooms in m2: 4072 iv. Floor area of supporting spaces in m2: 3161 (offices) v. Floor area of other spaces in m2: 15 878 | . Air temperature - summer and winter season (°C): 21°C +/-0.5°C ii. Relative humidity - summer and winter season (%): 35% +/- 5% iii. Air exchange (m3/h): iso7, iso8 iv. Air cleanliness (particles/ m3): iso7, iso8 v. Air overpressure (Pa): 45; 70 Pa | I. 34; -15; +/-5°C; II. 35-40; 75-80; +/-10% | n.a. | 50% electricity 70% of gas consumption approx | ISO7; ISO8 | attached | Steam humidifiers (HygroMatik) Cooling radiators, DX aggregates (CLH) G4,G7, F9 filters, HEPA filters | on a regular basis | yes | Desuperheater - CIAT LX4800 Plate heat recovery Rotary wheel heat exchanger | yes | The air exchange is 8-15 times the air volume of the room DMV Indoor unit: 454 | no |  |  |  | i. Annual LN2 consumption in liters*: 31,068 in CBM ii. Annual production of Helium in liters*: n.a. iii. Liquefier(s): model and capacity l/h: n.a. iv. Annual electric consumption of the liquefier(s): n.a. v. Annual external procurement of helium: n.a. | not yet | n.a. yet
3 | 2024-11-25 14:02 | 2024-11-28 22:22 | anonymous |  |  | ESS / Lund / Sweden | Siemens | 2021 and newer | 2021 | Diego CC | PXC | Bacnet/TCPIP | Bacnet | Modbus, dali, knx, mbus | Desigo cc | N/A | yes | VPN and jumpserver | for individuals | special network is used | by IT | internally | yes | opc (EON and Epic), modbus TCP | data are recorded periodically | no |  | no | via communications protocol | Mbus | yes |  | Recover heat from the facility; | cooling source | Cold side of the heat pump | NA | NA | no |  | yes | Knx | i: Campus ~18000, ii. Labs: ~12000, iii. Currently almost zero. iiii. Utility buildings: ~8000 v. Acc, Target, Instrument halls: ~57000, Also look at attachments | i. 20-24 ii. Not controlled iii. min air flow: 6.65 l/s.m2 iv. NA. v. NA. | +27 summer and -18 winter ii. 50% summer and 90 % winter | attachment will be sent separately | attachment will be sent separately | NA | attachment will be sent separately | For air humidity, there are two systems for dehumidification. A total of 219 larger and smaller systems. Air purification - filter the air to varying degrees depending on the space, HEPA filtering and simple pre-filter carpet. | on a regular basis | yes | Rotating heat exchanger | yes | 200 units | no |  |  |  | "Dear François, Philipp, group leader for the cryogenics at ESS/AD, shared the following values for the helium and nitrogen. The following are rough numbers of our LN2 procurements and LHe procurements for the past years. LHe is partially used to fill up the SCL and cryolines (to Target and tunnel), to Lund University and MAX IV (nothing recovered right now) but unfortunately mostly are losses due to commissioning activities and leaks. LN2 2021: 424 000 l 2022: 503 000 l 2023: 508 000 l 2024: the values would be availalbe in a week if needed. LHe 2021: 12 900 l 2022: 7 150 l 2023: 6 600 l 2024: 15 550 l Best regards, Mamad" | No | Leyla Abdullayeva, Serkan Ucer, Mamad Eshraqi